## Standard Permit GRA1
Generic risk assessment for standard rules set number SR2018 No 2 v1.0
Standard Facility: |  |  |  | Specified Generators, Tranche B low risk, base load operation 0-2 MW with high background Nox
Location: |  |  |  | Applies to all potential locations
Risk assessment carried out by: |  |  |  | Natural Resources Wales
Date: |  |  |  | 2018-10-03
The scope of the permit and associated rules is defined by the following risk criteria:
| Parameter 1 | Total aggregated thermal input of all Specified generators burning natural gas of less than 2 MW.
| Parameter 2 | The stack height shall be no less than 15 meters and must be vertical and unimpeded by cowls or caps, and at least 2 meters above the nearest building.
| Parameter 3 | The activities must not be carried out within 500 metres of a Special Area of Conservation (SAC), Special Protection Area (SPA), Ramsar Site or a Site of Special Scientific Interest (SSSI).
| Parameter 4 | The background NO2 concentration at sensitive human receptor must be less than 36 µg/m3.
| Abbreviations: | SR - Standard Rule
NOx - Oxides of nitrogen
NO2 - Nitrogen Dioxide
CO - Carbon Monoxide
CHP - Combined heat and power
SR (emissions of substances not controlled by emission limits) - emissions of substances .... shall not cause pollution…., with appropriate measures:
Data and information |  |  |  |  | Judgement |  |  | Action (by permitting)
Receptor | Source | Harm | Pathway | Probability of exposure | Consequence | Magnitude of risk | Justification for magnitude | Risk management | Residual risk
What is at risk? What do I wish to protect? | What is the agent or process with potential to cause harm? | What are the harmful consequences if things go wrong? | How might the receptor come into contact with the source? | How likely is this contact? | How severe will the consequences be if this occurs? | What is the overall magnitude of the risk? | On what did I base my judgement? | How can I best manage the risk to reduce the magnitude? | What is the magnitude of the risk after management? (This residual risk will be controlled by Compliance Assessment).
Local human population. | Releases of NOx | Harm to human health - respiratory irritation and illness. | Air transport then inhalation. | Low | Medium | Medium | There is potential for exposure to anyone living close to the site or at locations where members of the public might be regularly exposed. | Activities shall be managed and operated in accordance with a management system (will include inspection and maintenance of equipment, including engine management systems), point source emissions to air with emission limits for NOx. Secondary abatement can be fitted to achieve the emissions limit. A stack of at least 15 meters and 2 meters above the nearest building ensures good dispersion of NOx. The activities shall be carried out where the NO2 background is less than 36 µg/m3 ensuring the Environmental Standard protect human health is not exceeded at any ground level loaction. | Low
Protected nature conservation sites - SACs,SPAs, Ramsar sites and SSSIs. | Releases of NOx | Harm to protected site through toxic contamination, nutrient enrichment, disturbance etc. | Air transport and deposition. | Low | Medium | Low | Emissions to air may cause harm to and deterioration of nature conservation sites. | Emission limits for NOX are specified.At 500 metres or above, the potential hazards from the permitted activities pose a low risk to the broad sensitivity of species and habitats groups. The standard permit only applies at this distance or more. | Low
Notes: | Red triangle indicates comment containing supporting information
Yellow columns contain drop down menus that allow automatic evaluation of risk in green column
| Very low | Low | Medium
Very low | 1 | 2 | 3
Low | 2 | 4 | 6
Medium | 3 | 6 | 9
High | 4 | 8 | 12
Note on B25: Receptors to consider should include: atmosphere, land, surface waters, groundwater, humans, wildlife and their habitats. A single receptor may be at risk from several different sources and all must be addressed.
Note on C25: The Source of hazard will be the activity or operation taking place for which a particular hazard may arise.
Note on D25: Harm may arise when a specific hazard is realised.
Note on E25: Pathways are the routes or means by which defined hazards may potentially realise their consequences at the receptors.
Note on F25: Probability of exposure is the likelihood of the receptors being exposed to the hazard. Example definitions: High – exposure is probable: direct exposure likely with no / few barriers between hazard source and receptor; Medium – exposure is fairly probable: feasible exposure possible - barriers to exposure less controllable; Low – exposure is unlikely: several barriers exist between hazards source and receptors to mitigate against exposure: Very Low – exposure is very unlikely: effective, multiple barriers in place to mitigate against exposure.
Note on G25: The consequences of a hazard being realised may be actual or potential harm. This will include be on a high/medium/low/very low score using attributes and scaling to consider 'harm'.
Note on H25: Magnitude of the risk is determined by combining the probability with the magnitude of the potential consequences High risks require additional assessment and active management Medium risks require additional assessment and may require active management/monitoring Low and very low risks require periodic review.
Note on J25: Risk management involves breaking or limiting the source-pathway-receptor linkage to reduce risk.